Thank you for using our product,  controller is compatible with a variety of operating modes,  LED digital tube displays, procedures for intelligent control, to achieve the timing relay functions,the voltage control function, and voltmeter functions, applies to applies to automatic control field, product testing, DIY etc.

This product is designed to meet electrical safety rules, with industrial reliability, it meet a variety of control requirements at lowest price .

Features

Operating modes:

P-1:  Timer ( 1-999 S)

P-2:  Delay timer( 1-999 S)

P-3:  Voltage control relay( control the load on/off)

P-4:  Voltage control Timer (pull first)

Timing Range : 0 0-999 seconds or 0-999 minutes,

Voltmeter display range :DC 0-99 .9 V

Voltage detection error: ± 0.1V

Operating Power: DC10-15V

Relay parameters:

Coil Voltage: DC 12V

A set of conversion (normally open and normally closed)

Contact load: 10A/277V AC or 10A/30V DC

Contact resistance: ≤ 100mΩ (1A 6VDC)

Mechanical durability: 10 millions

Electricity Durability:> 100,000 (10A-250VAC)

Operating Temperature: -40 ~ 85℃

external signal input: (0-12V) or passive switch (can be set to 9 files delay time)

Timer mode can set the relay contact pull and release time, the implementation of a single timing loop

In voltage control mode ,can preset upper and lower voltage vlaue limits

Discrete patch digital tube, to facilitate the demolition in order to reduce power consumption

The pre-set parameters can be saved after power cut down.

1.1 Timer mode (P-1)

Press the “SET” button to select "P-1" ,controller system will enter the timer mode.

“P-1”:   1-999    seconds /minute can be set.

Cyclic run:

In the timer mode, the user can set the relay’s pull-in time T1 and the release time T2, such as setting T1 for 3 seconds, T2 for 7 seconds, then the relay will be run executed first  three seconds of the pull-in and then 7 seconds of release, cyclic run.

User also can set cyclic times.

When you have set the value of the T1 and T2 , the system saved the settings, the next time system will be loaded automatically T1 time to wait to start running.

Timer:

If you set T1 with a specified time, set T2 (release time) with 0, the relay will stop after the timer run T1 time, no longer running, it can be used as a timer, with running time end, the normally open contact of relay release, then press the “ENTER” button, the system re-start the timer for T1 time.

In timer state , you can use external switch or pulse signal input Interface ( Figure 1)on controller to start the timer.

Timer setting steps:

1) For the first time of set , select "P-1” time relay mode, LED digital tube display" 000 ";

2) Press the “SET” button, system will enter the T1 time value settings first, the digital that wait for set  flashing with 1HZ frequency, press “ENTER” to select the appropriate value, then press the “SET” button for three times to enter the T2 time value settings, and cyclic times , press the “SET” button to exit the set state, the system waits to press “enter” to start running.

3)	In the time setting state ,time value can be switched in minutes unit or second unit, press the “SET” button to enter the time set by state (set LED digital tube flashing) ,at this time Press the “SET” button for 3 seconds to release ,the LED digital tube will light the right decimal points, it means that timing value with minutes unit, if the decimal point is not light, it means that timing value with seconds unit.

After set is completed, press the “SET” button to exit the setting state , press “ENTER” to start timing, if timing value is set with seconds unit, seconds value will display with countdown form. If timing value is set with minute unit,  the right decimal point flashing with 1HZ frequency, means the countdown is running. While timer is running, the normally open contact of relay connected, the normally closed contact of relay disconnect, press the “ENTER” to halt  run ,press the “ENTER” for three seconds to return mode selection state  “P-0”.

1.2  Delay timer (P-2)

The Setting method of “P- 2” is the same as “P- 1”,in the mode of  “P-2”, the relay will first execute a release of  T1 time then pull with T2 time.

1.3  Voltage control relay mode (P-3)

In mode selection state(“P-0”), press the “SET” button to select "P-3", then press the “ENTER” to enter the voltage comparison control mode, the controller will detect voltage from “VOL” Interface ( Figure 1)and display value (DC 0-99.9V),it also can be used as a DC voltmeter ,the default initial run state relay contact is pull (normally closed contact is disconnected, normally open switch on), press the “SET “button to set the three values, the LED digital tube is set to flashing with1Hz frequency, first to be set upper limit voltage value , press the “SET” button three times, lower limit value of voltage to be set, press the “ENTER” button to increase value, the lower limit voltage can not exceed the upper limit, press the “SET” button to make digital tube is no longer flashing, this time into voltage control mode , the controller detecting DC voltage from external input Interface ( Figure 1) , when detects voltage exceeds the upper limit of the pre-set voltage, the relay release ( normally  closed contact connect , normally open contact disconnect), until the voltage drops below the lower limit pre-set voltage, the relay will re-pull ( normally open contact connect ,normally closed disconnect ).

If the pre-set voltage upper and lower limits set to the same, such as 5.0V, when controller detected voltage value at 5.0 fluctuations may cause the relay contact frequent

action, We recommend to set the voltage to maintain the difference between the upper and lower limits.

The factory default setting, is relay released for a voltage exceeding the upper limit , the relay re-pull when the voltage is below the lower limit  , if you want the voltage exceeds the limit relay to connect the load, please select in the following two ways to:

1) In” P-3” mode, press the “SET” button for three seconds then release the button, the contact of relay state will be negated.

2) Load connected to the normally closed contact and common, so that limited release of the relay on the detected voltage exceeds the normally open contact disconnect,

Note: The detection voltage terminal access to reliable, have not loose wiring around the circuit board insulation ,may lead to the induced voltage detection value is not accurate.